## Sheet1
P.U.
R | X | Z | Farm rating
0.00684 | 0.041338 | 0.0419 | 121
V_base | S_base | Z_base
220 | 100 | 484
value
Z | S
20.2796 | 2386.6309
SCR
19.7242 | =short rating/farm rating"
6.0436

## Sheet2
system base
Base Voltage (kV) | Base Power (MVA) | Base impedance (Ohm) | frequency (Hz) | plant rating (MVA)
132 | 100 | 174.24 | 50 | 83.6
if impedance is known
Thevenin R (Ohm) | Thevenin X(Ohm) | equivalent X (Henry) | Thevenin Z(OhM) | X/R ratio
66.2112 | 165.8765 | 0.528 | 178.6027 | 2.5053
Thevenin R (pu) | Thevenin X(pu) | equivalent X (pu) | Thevenin Z(pu) | X/R ratio
0.38 | 0.952 | -- | 1.025 | 2.5053
SCR calculation
Fault Level (MVA) | SCR
97.5573 | 1.167
if SCR and X/R ratio is known
Thevenin R (Ohm) | Thevenin X(Ohm) | equivalent X (Henry) | Thevenin Z(OhM) | X/R ratio
7.5308 | 21.7639 | 0.069277 | 23.03 | 2.89
Thevenin R (pu) | Thevenin X(pu) | equivalent X (pu) | Thevenin Z(pu) | X/R ratio
0.043221 | 0.12491 | -- | 0.13217 | 2.89
SCR calculation
Fault Level (MVA) | SCR
756.58 | 9.05
[5 empty] | z | 0.11649 | x/r | 2.1734
if SCR and X/R ratio is known
[5 empty] | Thevenin R (Ohm) | Thevenin X(Ohm) | equivalent X (Henry) | Thevenin Z(OhM) | X/R ratio
[5 empty] | 0.04869 | 0.10582 | #DIV/0! | 0.11649 | 2.1734
[5 empty] | Thevenin R (pu) | Thevenin X(pu) | equivalent X (pu) | Thevenin Z(pu) | X/R ratio
[5 empty] | 0.04869 | 0.10582 | -- | 0.11649 | 2.1734
SCR calculation
[5 empty] | Fault Level (MVA) | SCR
[5 empty] | 0 | 9.05

## Sheet3
Parameter | Value | Unit |  |  |  | Parameter | Value | Unit
Rated capacity | 75 | MVA |  |  |  | Number of transformers | 19 | Qty
Winding 1 nominal | 132 | kV |  | 14.52 | 10.89 | Transformer rated capacity | 4.4 | MVA
Winding 2 nominal | 33 | kV |  | 0.37333 |  | Equivalent transformer rating | 83.6 | MVA
Specified R | 0.28 | % on 75 MVA base | 0.37333 |  |  | Winding 1 nominal | 33 | kV
Specified X | 12.5 | % on 75 MVA base | 16.6667 |  |  | Winding 2 nominal | 0.66 | kV
R-Zero | 0.28 | % on 75 MVA base | 0.37333 |  |  | Specified R | 0.65 | % on 83.6 MVA base | 0.77751
X-Zero | 12.5 | % on 75 MVA base | 16.6667 |  |  | Specified X | 6.5 | % on 83.6 MVA base | 7.7751
Vector group | Dyn11 | Text |  |  |  | R-Zero | 0.4018 | % on 83.6 MVA base | 0.48062
HV-LV winding angle | -30 | o |  |  |  | X-Zero | 4.018 | % on 83.6 MVA base | 4.8062
Tap changer type | On-load | Text |  |  |  | Vector group | Dy11 | Text
Tap changer winding | HV | Text |  |  |  | HV-LV winding angle | -30 | o
Controlled bus | LV | Text |  |  |  | Tap change type | Off-load | Text
Number of taps | 17 | Qty |  |  |  | Number of taps | 5 | Qty
Tap change step size | 1.25 | % |  |  |  | Tap changer step size | 2.5 | %
R1max | 1.1 | pu | 145.2 |  |  | R1max | 1.05 | pu
R1min | 0.9 | pu | 118.8 |  |  | R1min | 0.95 | pu
Vmax | 1.02 | pu | 134.64 |  |  | Tap setting (HV:LV) | 1:01 | Text
Vmin | 1 | pu
Maximum fault level at PoC is 882.5 MVA in PIA, designed ac circuit breaker capacity is 2 kA in SLD? Confirm?
Suggest this is a typo and should be 20 kA.